{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":77,"n_cols":14,"rows_kept":77,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","LREQ-BY1"]
[]
[]
[]
[]
["","","","","","LREQ5B7Y1","LREQ6B7Y1","LREQ8B7Y1","LREQ10B7Y1","LREQ12B7Y1","LREQ15B7Y1","LREQ20B7Y1","LREQ30B7Y1","LREQ40B7Y1"]
["Puissance frigorifique","Puissance frigorifique-=-Basse température","","Puissance frigorifique-=-Basse température-=-Nom.-=-kW","kW","5.51 (2)","6.51 (2)","8.33 (2)","10.0 (2)","10.7 (2)","13.9 (2)","15.4 (2)","27.8","29.6"]
["","Puissance frigorifique-=-Moyenne température","","Puissance frigorifique-=-Moyenne température-=-Nom.-=-kW","kW","12.5 (1)","15.2 (1)","19.8 (1)","23.8 (1)","26.5 (1)","33.9 (1)","37.9 (1)","67.8 (3)","75.8 (3)"]
["Puissance absorbée","Puissance absorbée-=-Basse température","","Puissance absorbée-=-Basse température-=-Nom.-=-kW","kW","4.65 (2)","5.88 (2)","7.72 (2)","9.27 (2)","9.89 (2)","12.8 (2)","14.1 (2)","25.6","27.6"]
["","Puissance absorbée-=-Moyenne température","","Puissance absorbée-=-Moyenne température-=-Nom.-=-kW","kW","5.1","6.56 (1)","8.76 (1)","10.6 (1)","12.0 (1)","15.2 (1)","17.0 (1)","30.4","34.0"]
["Plage de fonctionnement","Plage de fonctionnement-=-Température extérieure","","Plage de fonctionnement-=-Température extérieure-=-Min.-=-°C","°C","-20","-20","-20","-20","-20","-20","-20"]
["","","","Plage de fonctionnement-=-Température extérieure-=-Max.-=-°C","°C","43","43","43","43","43","43","43"]
["","Plage de fonctionnement-=-Évaporateur","Plage de fonctionnement-=-Évaporateur-=-Rafraîchissement","Plage de fonctionnement-=-Évaporateur-=-Rafraîchissement-=-Min.-=-°CBS","°CDB","-45","-45","-45","-45","-45","-45","-45"]
["","","","Plage de fonctionnement-=-Évaporateur-=-Rafraîchissement-=-Max.-=-°CBS","°CDB","10","10","10","10","10","10","10"]
["Consommation électrique annuelle Q","Consommation électrique annuelle Q-=-R-410A","","Consommation électrique annuelle Q-=-R-410A-=-Te -10°C-=-kWh/a","kWh/a","19907","24681","33483","42794","46377","61683","72030"]
["","","","Consommation électrique annuelle Q-=-R-410A-=-Te -35°C-=-kWh/a","kWh/a","22805","27453","33817","39747","44363","61090","67325"]
["Taux de performance énergétique saisonnier SEPR","Taux de performance énergétique saisonnier SEPR-=-R-410A","","Taux de performance énergétique saisonnier SEPR-=-R-410A-=-Te -10°C","","3.86","3.79","3.64","3.42","3.51","3.38","3.23"]
["","","","Taux de performance énergétique saisonnier SEPR-=-R-410A-=-Te -35°C","","1.80","1.77","1.84","1.88","1.80","1.70","1.70"]
["Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -10&nbsp;°C","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -10&nbsp;°C-=-Puiss. frigorifique nominale (PA)-=-kW","kW","12.50","15.20","19.80","23.80","26.50","33.90","37.90"]
["","","","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -10&nbsp;°C-=-Puissance absorbée nominale (DA)-=-kW","kW","5.10","6.56","8.76","10.60","12.00","15.20","17.00"]
["","","","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -10&nbsp;°C-=-COP nominal (COPA)","","2.45","2.32","2.26","2.25","2.21","2.23","2.23"]
["","","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -35°C","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -35°C-=-Puiss. frigorifique nominale (PA)-=-kW","kW","5.51","6.51","8.33","10.00","10.70","13.90","15.40"]
["","","","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -35°C-=-Puissance absorbée nominale (DA)-=-kW","kW","4.65","5.88","7.72","9.27","9.89","12.80","14.10"]
["","","","Paramètres à pleine charge à temp. ext. 32&nbsp;°C (Point A)-=-R-410A-=-Te -35°C-=-COP nominal (COPA)","","1.18","1.11","1.08","1.08","1.08","1.09","1.09"]
["Paramètres à pleine charge à temp. ext. 43°C","Paramètres à pleine charge à temp. ext. 43°C-=-R-410A","Paramètres à pleine charge à temp. ext. 43°C-=-R-410A-=-Te -10&nbsp;°C","Paramètres à pleine charge à temp. ext. 43°C-=-R-410A-=-Te -10&nbsp;°C-=-COP déclaré (COP3)","","1.54","1.57","1.40","1.46","1.47","1.46","1.51"]
["","","Paramètres à pleine charge à temp. ext. 43°C-=-R-410A-=-Te -35°C","Paramètres à pleine charge à temp. ext. 43°C-=-R-410A-=-Te -35°C-=-COP déclaré (COP3)","","0.76","0.74","0.68","0.70","0.71","0.71","0.74"]
["Compressor 2","Type","","","","","","Compresseur scroll hermétique","Compresseur scroll hermétique","Compresseur scroll hermétique","Compresseur scroll hermétique","Compresseur scroll hermétique"]
["Moteur de ventilateur","Moteur de ventilateur-=-Entraînement","","","","Entraînement direct","Entraînement direct","Entraînement direct","Entraînement direct","Entraînement direct","Entraînement direct","Entraînement direct"]
["Moteur de ventilateur 2","Moteur de ventilateur 2-=-Sortie-=-W","","","W","","","","","","350","750"]
["Ventilateur","Ventilateur-=-Quantité","","","","1","1","1","1","1","2","2"]
["","Ventilateur-=-Type","","","","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice","Ventilateur à hélice"]
["","Ventilateur-=-Débit d'air","Ventilateur-=-Débit d'air-=-Rafraîchissement","Ventilateur-=-Débit d'air-=-Rafraîchissement-=-Nom.-=-m³/min","m³/min","95","102","171","179","191","230","240"]
["Moteur de ventilateur","Moteur de ventilateur-=-Sortie-=-W","","","W","350","350","750","750","750","350","750"]
["Raccords de tuyauterie","Raccords de tuyauterie-=-Liquide","","Raccords de tuyauterie-=-Liquide-=-50 m ou moins","","ø 9,5 C1220T (Raccord brasé)","ø 9,5 C1220T (Raccord brasé)","ø 9,5 C1220T (Raccord brasé)","ø 9,5 C1220T (Raccord brasé)","ø 12,7 C1220T (Raccord brasé)","ø 12,7 C1220T (Raccord brasé)","ø 12,7 C1220T (Raccord brasé)","ø 19,05 C1220T (raccordement à braser)","ø 19,05 C1220T (raccordement à braser)"]
["","","","Raccords de tuyauterie-=-Liquide-=-50~130 m","","Ø 9.5 C1220T (Brazing connection)","Ø 9.5 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","Ø 12.7 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)","ø 19.05 C1220T (Brazing connection)"]
["","Raccords de tuyauterie-=-Gaz","","Raccords de tuyauterie-=-Gaz-=-50 m ou moins","","ø 22,2 C1220T (Raccord brasé)","ø 22,2 C1220T (Raccord brasé)","ø 28,6 C1220T (Raccord brasé)","ø 28,6 C1220T (Raccord brasé)","ø 28,6 C1220T (Raccord brasé)","ø 34,9 C1220T (Raccord brasé)","ø 34,9 C1220T (Raccord brasé)","ø 41,28 C1220T (raccordement à braser)","ø 41,28 C1220T (raccordement à braser)"]
["","","","Raccords de tuyauterie-=-Gaz-=-50~130 m","","ø 22.2 C1220T (Brazing connection)","ø 22.2 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","Ø 28.6 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 34.9 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)","ø 41.28 C1220T (Brazing connection)"]
["Dimensions","Dimensions-=-Unité","","Dimensions-=-Unité-=-Hauteur-=-mm","mm","1680","1680","1680","1680","1680","1680","1680"]
["","","","Dimensions-=-Unité-=-Largeur-=-mm","mm","635","635","930","930","930","1240","1240"]
["","","","Dimensions-=-Unité-=-Profondeur-=-mm","mm","765","765","765","765","765","765","765"]
["Poids","Poids-=-Unité-=-kg","","","kg","166","166","242","242","242","331","337"]
["Réfrigérant","","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["Caisson","Caisson-=-Couleur","","","","Blanc ivoire (code Munsell : 5Y7,5/1)","Blanc ivoire (code Munsell : 5Y7,5/1)","Blanc ivoire (code Munsell : 5Y7,5/1)","Blanc ivoire (code Munsell : 5Y7,5/1)","Blanc ivoire (code Munsell : 5Y7,5/1)","Blanc ivoire (code Munsell : 5Y7,5/1)","Blanc ivoire (code Munsell : 5Y7,5/1)"]
["Réfrigérant","Réfrigérant-=-PRP","","","","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5","2087.5"]
["Échangeur de chaleur","Échangeur de chaleur-=-Type","","","","Échangeur à ailettes transversales","Échangeur à ailettes transversales","Échangeur à ailettes transversales","Échangeur à ailettes transversales","Échangeur à ailettes transversales","Échangeur à ailettes transversales","Échangeur à ailettes transversales"]
["Réfrigérant","Réfrigérant-=-Charge-=-kg","","","kg","5.2","5.2","7.9","7.9","7.9","11.5","11.5"]
["","Réfrigérant-=-Charge-=-TCO2Eq","","","tCO2Eq","10.9","10.9","16.5","16.5","16.5","24.0","24.0"]
["Standard Accessories","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Clamping materials","","","","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials","Clamping materials"]
["","Refrigerant label for F-gas regulation","","","","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation","Refrigerant label for F-gas regulation"]
["","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Connection pipes","","","","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes","Connection pipes"]
["","Additional refrigerant label","","","","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label","Additional refrigerant label"]
["Alimentation électrique","Alimentation électrique-=-Phase","","","","3~","3~","3~","3~","3~","3~","3~"]
["","Alimentation électrique-=-Fréquence-=-Hz","","","Hz","50","50","50","50","50","50","50"]
["","Alimentation électrique-=-Tension-=-V","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Courant","Courant-=-Courant nominal de fonctionnement - 50Hz","Courant-=-Courant nominal de fonctionnement - 50Hz-=-Compresseur 2","Courant-=-Courant nominal de fonctionnement - 50Hz-=-Compresseur 2-=-Rafraîchissement-=-A","A","","","7.5","7.9","8.3","8.2","8.4"]
["","","Courant-=-Courant nominal de fonctionnement - 50Hz-=-Compresseur 1","Courant-=-Courant nominal de fonctionnement - 50Hz-=-Compresseur 1-=-Rafraîchissement-=-A","A","7.1","9.2","5.3","7.4","9.8","7.0","9.5"]
["","","Courant-=-Courant nominal de fonctionnement - 50Hz-=-Compresseur 3","Courant-=-Courant nominal de fonctionnement - 50Hz-=-Compresseur 3-=-Rafraîchissement-=-A","A","","","","","","8.2","8.4"]
["Notes","","","","","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Cooling: evaporating temp. -10°C; outdoor temp. 32°C; suction SH10°C","(1) - Lorsque la température d'évaporation cible est de -20 °C ou moins, il est possible d'ajouter de l'huile réfrigérante. En cas d'ajout d'huile réfrigérante, la température d'évaporation cible ne peut pas changer pour passer à -20 °C ou plus.","(1) - Lorsque la température d'évaporation cible est de -20 °C ou moins, il est possible d'ajouter de l'huile réfrigérante. En cas d'ajout d'huile réfrigérante, la température d'évaporation cible ne peut pas changer pour passer à -20 °C ou plus."]
["","","","","","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Cooling: evaporating temp. -35°C; outdoor temp. 32°C; suction SH10°C","(2) - Dans un environnement d'utilisation où la température extérieure chute en dessous de -10 °C, l'installation d'une planche pare-vent ou d'un capot de  protection contre la neige est nécessaire. Pour en savoir plus, se reporter au manuel d'entretien.","(2) - Dans un environnement d'utilisation où la température extérieure chute en dessous de -10 °C, l'installation d'une planche pare-vent ou d'un capot de  protection contre la neige est nécessaire. Pour en savoir plus, se reporter au manuel d'entretien."]
["","","","","","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Données de pression sonore : mesure réalisée 1 m devant l'unité, à 1,5 m de hauteur","(3) - Conditions de fonctionnement de l'unité extérieure : température d'évaporation = -10 °C, température extérieure +32 °C, surchauffe d'aspiration 10K","(3) - Conditions de fonctionnement de l'unité extérieure : température d'évaporation = -10 °C, température extérieure +32 °C, surchauffe d'aspiration 10K"]
["","","","","","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - RLA is based on following conditions: outdoor temp. 32°CDB; suction SH 10°C; saturated temperature equivalent to suction pressure -10°C","(4) - Le kit tuyau d'embranchement (EKHRQZM) doit être utilisé pour diviser un tuyau d'aspiration entre les unités extérieures.","(4) - Le kit tuyau d'embranchement (EKHRQZM) doit être utilisé pour diviser un tuyau d'aspiration entre les unités extérieures."]
["","","","","","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - TOCA means the total value of each OC set.","(5) - Utiliser l'huile réfrigérante des pièces de rechange DAIKIN. (bidon d'1 litre : réf. 5004333)","(5) - Utiliser l'huile réfrigérante des pièces de rechange DAIKIN. (bidon d'1 litre : réf. 5004333)"]
["","","","","","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - MSC means the maximum current during start up of the compressor","(6) - La valeur RLA est basée sur les conditions suivantes : température extérieure : 32 °C ; surchauffe d'aspiration 10 K ; température d'évaporation -10 °C.","(6) - La valeur RLA est basée sur les conditions suivantes : température extérieure : 32 °C ; surchauffe d'aspiration 10 K ; température d'évaporation -10 °C."]
["","","","","","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set."]
["","","","","","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Maximum allowable voltage range variation between phases is 2%.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(8) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Select wire size based on the larger value of MCA or TOCA","(9) - Maximum allowable voltage range variation between phases is 2%.","(9) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Minimum Ssc (=Short-circuit power) value: Equipment complying with EN 61000-3-2","(11) - Compresseurs 2 et 3","(11) - Compresseurs 2 et 3"]
["","","","","","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1","(12) - Compressor 1"]
["","","","","","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2","(13) - Compressor 2"]
["","","","","","(14) - Compresseurs 2 et 3","(14) - Compresseurs 2 et 3","(14) - Compresseurs 2 et 3","(14) - Compresseurs 2 et 3","(14) - Compresseurs 2 et 3","(14) - Compresseurs 2 et 3","(14) - Compresseurs 2 et 3"]
["","","","","","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit","(15) - Factory charge of unit"]
["","","","","","(16) - Contient des gaz à effet de serre fluorés.","(16) - Contient des gaz à effet de serre fluorés.","(16) - Contient des gaz à effet de serre fluorés.","(16) - Contient des gaz à effet de serre fluorés.","(16) - Contient des gaz à effet de serre fluorés.","(16) - Contient des gaz à effet de serre fluorés.","(16) - Contient des gaz à effet de serre fluorés."]
["","","","","","(17) - Réglementation Ecodesign : (UE) 2015/1095","(17) - Réglementation Ecodesign : (UE) 2015/1095","(17) - Réglementation Ecodesign : (UE) 2015/1095","(17) - Réglementation Ecodesign : (UE) 2015/1095","(17) - Réglementation Ecodesign : (UE) 2015/1095","(17) - Réglementation Ecodesign : (UE) 2015/1095","(17) - Réglementation Ecodesign : (UE) 2015/1095"]
["Standard Accessories","Ref. oil fill volume label","","","","","","","","","","","Ref. oil fill volume label","Ref. oil fill volume label"]